## Motor Calculator
NEMA Motor Data Calculator
BASED ON THE 2005 NEC
[5 empty] | Three Phase |  |  | Single Phase
Horse Power
[8 empty] | 115V | 230V
[8 empty] | 4.4 | 2.2 | Full Load Amps (FLA)
|  |  |  | 6 | Full Load Amps (FLA) |  |  | 14 | 14 | Wire Size
|  |  |  | 14 | Wire Size |  |  | 15 | 15 | Thermal Breaker Size
|  |  |  | 15 | Thermal Breaker Size |  |  | FAL12015 | FAL22015 | Breaker Cat No.
|  |  |  | FAL32015 | Breaker Cat No. |  |  | H221N | H221N | HD Switch Nema 1 Enclosed
|  |  |  | H321N | HD Switch, Nema 1 Enclosed |  |  | 6.25 | 3.2 | Dual Elem Time Delay Fuse Amps
|  |  |  | 10 | Dual Elem Time Delay Fuse Amps |  |  | FG-2 | FG-2 | Fractional HP N1 Starter Class 2510
|  | Class | 8536 | SAG-12 | Nema Starter Catalog Number |  |  | A4.32 | A1.86 | Thermal Unit
|  |  |  | B9.10 | Melting Alloy Thermal Unit |  |  | MBG-1 | MBG-1 | Integral Starter N1 Enc 2510
|  |  |  | 00 | Nema Size Starter |  |  | B4.15 | B2.10 | One Melting Alloy Thermal Unit
[8 empty] | SAG-11 | SAG.11 | NEMA Enclosed Starter Class 8536
Coil Voltage Code - Digest Page 14-15 | [7 empty] | B4.85 | B2.40 | Thermal Unit
Add to the end of the Part No
60Hz | 50Hz | Code | [8 empty] | Scheduler
24 | … | V01 |  | Transformer Data | [6 empty] | Enter Start Date (1/1/05)
120 | 110 | V02 |  |  |  | = Single Phase | = Three Phase |  |  |  | 2005-01-01
208 | … | V08 |  | KVA | Voltage | Amps | Amps
240 | 220 | V03 | [8 empty] | Enter Number of Weeks
480 | 440 | V06 | [8 empty] | 0
600 | 550 | V07 | Enter KVA | and | Enter Voltage
Special Voltage |  | V99 | [8 empty] | End Date
S- is for separate control |  |  |  | Click here for Wire & Cable | [6 empty] | 2005-01-01
Voltage
Horse Power

## Wire Data (hidden)
0 | 100
20
#14 | A | 14 | 12 | 10 | 8 | 6 | 4 | 3 | 2 | 1 | 1/0 | 2/0 | 3/0 | 4/0 | 250 | 300 | 350 | 400 | 500 | 600 | 700 | 750 | 800 | 900 | 1000
#12 | B | 20 | 25 | 35 | 50 | 65 | 85 | 100 | 115 | 130 | 150 | 175 | 200 | 230 | 255 | 285 | 310 | 335 | 380 | 420 | 460 | 475 | 490 | 520 | 545
#10 | C | 1/2 | 1/2 | 1/2 | 3/4 | 3/4 | 1 | 1 | 1 1/4 | 1 1/4 | 1 1/2 | 1 1/2 | 2 | 2 | 2 | 2 1/2 | 2 1/2 | 2 1/2 | 2 1/2 | 3 | 3 | 3 | 3 | 3 1/2 | 3 1/2
#8 | D | 1/2 | 1/2 | 3/4 | 3/4 | 1 | 11/4 | 1 1/4 | 1 1/4 | 1 1/2 | 2 | 2 | 2 | 2 1/2 | 2 1/2 | 2 1/2 | 2 1/2 | 3 | 3 | 3 1/2 | 3 1/2 | 3 1/2 | 4 | 4 | 4
#6 | E | 1/2 | 1/2 | 1/2 | 1/2 | 3/4 | 1 | 1 | 1 | 1 1/4 | 1 1/4 | 1 1/2 | 1 1/2 | 2 | 2 | 2 | 2 1/2 | 2 1/2 | 2 1/2 | 3 | 3 | 3 | 3 | 3 | 3 1/2
#4 | F | 1/2 | 1/2 | 1/2 | 3/4 | 3/4 | 1 | 1 1/4 | 1 1/4 | 1 1/4 | 1 1/2 | 2 | 2 | 2 | 2 1/2 | 2 1/2 | 2 1/2 | 2 1/2 | 3 | 3 | 3 1/2 | 3 1/2 | 3 1/2 | 4 | 4
#3 | G | N/A | N/A | N/A | 40 | 50 | 65 | 75 | 90 | 100 | 120 | 135 | 155 | 180 | 205 | 230 | 250 | 270 | 310 | 340 | 375 | 385 | N/A | N/A | 445
#2 | H | N/A | N/A | N/A | 3/4 | 3/4 | 1 | N/A | 1 | 1 1/4 | 1 1/4 | 1 1/2 | 1 1/2 | 2 | 2 | 2 | 2 1/2 | 2 1/2 | 2 1/2 | 3 | 3 | 3 | N/A | N/A | 3 1/2
#1 | I | N/A | N/A | N/A | 3/4 | 1 | 1 | N/A | 1 1/4 | 1 1/2 | 1 1/2 | 2 | 2 | 2 | 2 1/2 | 2 1/2 | 2 1/2 | 2 1/2 | 3 | 3 | 3 1/2 | 3 1/2 | N/A | N/A | 4
1/0 | J | N/A | N/A | N/A | 1/2 | 3/4 | 3/4 | N/A | 1 | 1 1/4 | 1 1/4 | 1 1/4 | 1 1/2 | 1 1/2 | 2 | 2 | 2 | 2 1/2 | 2 1/2 | 2 1/2 | 3 | 3 | N/A | N/A | 3
2/0 | K | N/A | N/A | N/A | 3/4 | 3/4 | 1 | N/A | 1 1/4 | 1 1/4 | 1 1/2 | 1 1/2 | 2 | 2 | 2 | 2 1/2 | 2 1/2 | 2 1/2 | 2 1/2 | 3 | 3 | 3 | N/A | N/A | 4
3/0 | L | 0.58 | 0.37 | 0.23 | 0.15 | 0.095 | 0.061 | 0.048 | 0.04 | 0.032 | 0.027 | 0.022 | 0.017 | 0.015 | 0.013 | 0.012 | 0.010 | 0.0094 | 0.0082 | 0.0074 | 0.0068 | 0.0066 | - | - | -
4/0 | M | 0.5 | 0.31 | 0.20 | 0.13 | 0.084 | 0.055 | 0.045 | 0.037 | 0.03 | 0.027 | 0.022 | 0.018 | 0.016 | 0.014 | 0.013 | 0.012 | 0.011 | 0.0098 | 0.0092 | 0.0085 | 0.0084 | - | - | -
250 | N | 0.5 | 0.32 | 0.20 | 0.13 | 0.082 | 0.053 | 0.042 | 0.035 | 0.028 | 0.023 | 0.019 | 0.015 | 0.013 | 0.011 | 0.01 | .0088 | 0.0081 | 0.0071 | 0.0064 | 0.0059 | 0.0057 | - | - | -
300 | O | 0.43 | 0.27 | 0.17 | 0.11 | 0.073 | 0.048 | 0.039 | 0.032 | 0.026 | 0.023 | 0.019 | 0.016 | 0.014 | 0.012 | 0.011 | 0.010 | 0.0095 | 0.0085 | 0.0080 | 0.0074 | 0.0073 | - | - | -
350
400 | #8 XHHW and XHHW-2 CU requires 3/4" conduit for 3 wires
500 | #6 XHHW and XHHW-2 CU Requires 1" conduit for 4 wires
600 | 750 kcmil AL SHHW and XHHW-2 requires 3 1/2 conduit for 4 Wires
700
750
800
900
1000

## Data (hidden)
| 208V | [30 empty] | HP |  | Voltage |  | Phase
| Horse Power | 0.5 | 0.75 | 1 | 1.5 | 2 | 3 | 5 | 7.5 | 10 | 15 | 20 | 25 | 30 | 40 | 50 | 60 | 75 | 100 | 125 | 150 | 200 | 225 | 250 | 300 | 350 | 400 | 450 | 500 | 600 | 1 | 0.5 hp | 1 | 200 (208) | 200 | 1-Phase | 2
A | FLA | 2.5 | 3.7 | 4.8 | 6.9 | 7.8 | 11 | 17.5 | 25.3 | 32.2 | 48.3 | 62.1 | 78.2 | 92 | 120 | 150 | 177 | 221 | 285 | 359 | 414 | 552 | [8 empty] | 2 | 0.75 hp | 2 | 230 (240) | 230 | 3-Phase
B | Wire Size | 14 | 14 | 14 | 14 | 14 | 14 | 12 | 10 | 8 | 6 | 4 | 3 | 2 | 1/0 | 3/0 | 4/0 | 300 | 500 | 2-4/0 | 2-300 | 2-500 | [8 empty] | 3 | 1 hp | 3 | 460 (480) | 460
C | Thermal Breaker Size | 15 | 15 | 15 | 15 | 15 | 20 | 35 | 50 | 60 | 90 | 100 | 110 | 125 | 175 | 200 | 250 | 300 | 400 | 600 | 600 | 800 | [8 empty] | 4 | 1.5 hp | 4 | 575 (600) | 575
D | Breaker Cat No. | FAL32015 | FAL32015 | FAL32015 | FAL32015 | FAL32015 | FAL32020 | FAL32035 | FAL32050 | FAL32060 | FAL32090 | FAL32100 | KAL36110 | KAL36125 | KAL36175 | LAL36200 | LAL36250 | LAL36300 | LAL36400 | MAL36600 | MAL36600 | MAL36800 | [8 empty] | 5 | 2 hp |  | Voltage |  | 230 | 2
E | HD Sw Nema 1 Encl | H321N | H321N | H321N | H321N | H321N | H321N | H321N | H322N | H322N | H322N | H323N | H323N | H324N | H324N | H324N | H325 | H325 | H325 | H326 | H326 | [9 empty] | 6 | 3 hp |  | HP |  | 1.5 hp | 4
F | Dual Elem TD Fuse Amps | 4 | 6.25 | 8 | 10 | 10 | 17.5 | 25 | 40 | 50 | 60 | 90 | 100 | 125 | 175 | 200 | 250 | 300 | 400 | 500 | 600 | [9 empty] | 7 | 5 hp | A | FLA |  |  | 6 | IF(AL9=1,VLOOKUP(AH11,DATA208,AL10+2),IF(AL9=2,VLOOKUP(AH11,DATA240,AL10+2),IF(AL9=3,VLOOKUP(AH11,DATA480,AL10+2),IF(AL9=4,VLOOKUP(AH11,DATA600,AL10+2),"N/A"))))
G | Magnetic Starter 8536 | SAG-12 | SAG-12 | SAG-12 | SAG-12 | SBG-2 | SBG-2 | SCG-3 | SCG-3 | SDG-1 | SEG-1 | SEG-1 | SEG-1 | SFG-1 | SFG-1 | SGG-1 | SGG-1 | SGG-1 | SHG-2 | SHG-2 | SHG-2 | SJG-2 | [8 empty] | 8 | 7.5 hp | B | Wire Size |  |  | 14 | IF(AL9=1,VLOOKUP(AH12,DATA208,AL10+2),IF(AL9=2,VLOOKUP(AH12,DATA240,AL10+2),IF(AL9=3,VLOOKUP(AH12,DATA480,AL10+2),IF(AL9=4,VLOOKUP(AH12,DATA600,AL10+2),"N/A"))))
H | Melting Alloy TU | B3.30 | B4.85 | B6.90 | B10.2 | B11.5 | B15.5 | B28.0 | B45 | B56 | CC74.6 | CC94.0 | CC143 | CC143 | CC180 | B3.70 | B4.15 | B5.50 | B2.65 | B3.30 | B4.15 | [9 empty] | 9 | 10 hp | C | Thermal Breaker Size |  |  | 15 | IF(AL9=1,VLOOKUP(AH13,DATA208,AL10+2),IF(AL9=2,VLOOKUP(AH13,DATA240,AL10+2),IF(AL9=3,VLOOKUP(AH13,DATA480,AL10+2),IF(AL9=4,VLOOKUP(AH13,DATA600,AL10+2),"N/A"))))
I | NEMA SIZE | 00 | 00 | 00 | 00 | 0 | 0 | 1 | 1 | 2 | 3 | 3 | 3 | 4 | 4 | 5 | 5 | 5 | 6 | 6 | 6 | N/A | [8 empty] | 10 | 15 hp | D | Breaker Cat No. |  |  | FAL32015 | IF(AL9=1,VLOOKUP(AH14,DATA208,AL10+2),IF(AL9=2,VLOOKUP(AH14,DATA240,AL10+2),IF(AL9=3,VLOOKUP(AH14,DATA480,AL10+2),IF(AL9=4,VLOOKUP(AH14,DATA600,AL10+2),"N/A"))))
| 240v | [29 empty] | 11 | 20 hp | E | HD Sw Nema 1 Encl |  |  | H321N | IF(AL9=1,VLOOKUP(AH15,DATA208,AL10+2),IF(AL9=2,VLOOKUP(AH15,DATA240,AL10+2),IF(AL9=3,VLOOKUP(AH15,DATA480,AL10+2),IF(AL9=4,VLOOKUP(AH15,DATA600,AL10+2),"N/A"))))
A | FLA | 2.2 | 3.2 | 4.2 | 6 | 6.8 | 9.6 | 15.2 | 22 | 28 | 42 | 54 | 68 | 80 | 104 | 130 | 154 | 192 | 248 | 312 | 360 | 480 | [8 empty] | 12 | 25 hp | F | Dual Elem TD Fuse Amps |  |  | 10
B | Wire Size | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 10 | 10 | 6 | 4 | 4 | 3 | 1 | 2/0 | 3/0 | 250 | 350 | 2-3/0 | 2-4/0 | 2-350 | [8 empty] | 13 | 30 hp | G | Magnetic Starter 8536 |  |  | SAG-12
C | Thermal Breaker Size | 15 | 15 | 15 | 15 | 15 | 20 | 30 | 45 | 60 | 80 | 90 | 100 | 110 | 150 | 200 | 225 | 250 | 350 | 450 | 600 | 800 | [8 empty] | 14 | 40 hp | H | Melting Alloy TU |  |  | B9.10
D | Breaker Cat No. | FAL32015 | FAL32015 | FAL32015 | FAL32015 | FAL32015 | FAL32020 | FAL32030 | FAL32045 | FAL32060 | FAL32080 | FAL32090 | FAL32100 | KAL36110 | KAL36150 | KAL36200 | LAL36225 | LAL36250 | LAL36350 | MAL36450 | MAL36600 | MAL36800 | [8 empty] | 15 | 50 hp | I | NEMA SIZE |  |  | 00
E | HD Sw Nema 1 Encl | H321N | H321N | H321N | H321N | H321N | H321N | H321N | H321N | H322N | H322N | H323N | H323N | H323N | H324N | H324N | H324N | H325 | H325 | H325 | H326 | H326 | [8 empty] | 16 | 60 hp
F | Dual Elem TD Fuse Amps | 4 | 5.6 | 8 | 10 | 10 | 15 | 25 | 30 | 40 | 60 | 80 | 100 | 100 | 150 | 200 | 200 | 300 | 350 | 400 | 500 | 600 | [8 empty] | 17 | 75 hp |  | Date
G | Magnetic Starter 8536 | SAG-12 | SAG-12 | SAG-12 | SAG-12 | SBG-2 | SBG-2 | SCG-3 | SCG-3 | SDG-1 | SDG-1 | SEG-1 | SEG-1 | SEG-1 | SFG-1 | SFG-1 | SGG-1 | SGG-1 | SGG-1 | SHG-2 | SHG-2 | SHG-2 | [8 empty] | 18 | 100 hp
H | Melting Alloy TU | B3.30 | B4.15 | B6.25 | B9.10 | B10.2 | B14. | B25. | B36. | B45. | B79. | CC87.7 | CC112. | CC156. | CC167. | CC208. | B3.70 | B4.15 | B6.25 | B3.0 | B3.30 | B4.85 | [8 empty] | 19 | 125 hp
I | NEMA SIZE | 00 | 00 | 00 | 00 | 0 | 0 | 1 | 1 | 2 | 2 | 3 | 3 | 3 | 4 | 4 | 5 | 5 | 5 | 6 | 6 | 6 | 7 | 7 | 7 | [5 empty] | 20 | 150 hp
| 480V | [29 empty] | 21 | 200 hp
A | FLA | 1.1 | 1.6 | 2.1 | 3.0 | 3.4 | 4.8 | 7.6 | 11 | 14 | 21 | 27 | 34 | 40 | 52 | 65 | 77 | 96 | 124 | 156 | 180 | 240 |  | 302 | 361 | 414 | 477 | 515 | 590 |  | 22 | 225 hp
B | Wire Size | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 10 | 10 | 8 | 8 | 6 | 4 | 3 | 1 | 2/0 | 3/0 | 4/0 | 350 | [8 empty] | 23 | 250 hp
C | Thermal Breaker Size | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 20 | 25 | 40 | 60 | 70 | 80 | 90 | 100 | 110 | 125 | 200 | 225 | 250 | 350 | [8 empty] | 24 | 300 hp
D | Breaker Cat No. | FAL34015 | FAL34015 | FAL34015 | FAL34015 | FAL34015 | FAL34015 | FAL34015 | FAL34020 | FAL34025 | FAL34040 | FAL34060 | FAL34070 | FAL34080 | FAL34090 | FAL34100 | KAL36110 | KAL36125 | KAL36200 | LAL36225 | LAL36250 | LAL36350 | [8 empty] | 25 | 350 hp
E | HD Sw Nema 1 Encl | H361 | H361 | H361 | H361 | H361 | H361 | H361 | H361 | H361 | H361 | H362 | H362 | H362 | H363 | H363 | H363 | H364 | H364 | H364 | H365 | H365 | [8 empty] | 26 | 400 hp
F | Dual Elem TD Fuse Amps | 2 | 3.2 | 4 | 5.6 | 6.25 | 8 | 15 | 20 | 20 | 30 | 40 | 50 | 60 | 80 | 100 | 100 | 150 | 175 | 200 | 250 | 350 | [8 empty] | 27 | 450 hp
G | Magnetic Starter 8536 | SAG-12 | SAG-12 | SAG-12 | SAG-12 | SAG-12 | SBG-2 | SBG-2 | SCG-3 | SCG-3 | SDG-1 | SDG-1 | SDG-1 | SEG-1 | SEG-1 | SEG-1 | SFG-1 | SFG-1 | SFG-1 | SGG-1 | SGG-1 | SGG-1 | [8 empty] | 28 | 500 hp
H | Melting Alloy TU | B1.45 | B2.40 | B3.00 | B4.15 | B4.85 | B6.90 | B11.5 | B17.5 | B25. | B32. | B45. | B62. | CC59.4 | CC81.5 | CC103. | CC112. | CC156. | CC196. | B3.70 | B4.15 | B6.25
I | NEMA SIZE | 00 | 00 | 00 | 00 | 00 | 0 | 0 | 1 | 1 | 2 | 2 | 2 | 3 | 3 | 3 | 4 | 4 | 4 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 7 | 7 | 7
600V
A | FLA | 0.9 | 1.3 | 1.7 | 2.4 | 2.7 | 3.9 | 6.1 | 9.0 | 11 | 17 | 22 | 27 | 32 | 41 | 52 | 62 | 77 | 99 | 125 | 144 | 192 |  | 242 | 289 | 336 | 382 | 412 | 472
B | Wire Size | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 12 | 10 | 10 | 8 | 6 | 6 | 4 | 3 | 1 | 2/0 | 3/0 | 250
C | Thermal Breaker Size | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 20 | 35 | 45 | 60 | 60 | 80 | 90 | 100 | 110 | 150 | 200 | 200 | 250
D | Breaker Cat No. | FAL36015 | FAL36015 | FAL36015 | FAL36015 | FAL36015 | FAL36015 | FAL36015 | FAL36015 | FAL36020 | FAL36035 | FAL36045 | FAL36060 | FAL36060 | FAL36080 | FAL36090 | FAL36100 | KAL36110 | KAL36150 | KAL36200 | LAL36200 | LAL36250
E | HD Sw Nema 1 Encl | H361 | H361 | H361 | H361 | H361 | H361 | H361 | H361 | H361 | H361 | H361 | H362 | H362 | H362 | H363 | H363 | H363 | H364 | H364 | H364 | H365
F | Dual Elem TD Fuse Amps | 1.8 | 2.5 | 3.2 | 4 | 5 | 6.25 | 10 | 15 | 20 | 25 | 30 | 40 | 50 | 60 | 80 | 90 | 100 | 150 | 175 | 200 | 300
G | Magnetic Starter 8536 | SAG-12 | SAG-12 | SAG-12 | SAG-12 | SAG-12 | SBG-2 | SBG-2 | SCG-3 | SCG-3 | SDG-1 | SDG-1 | SDG-1 | SEG-1 | SEG-1 | SEG-1 | SFG-1 | SFG-1 | SFG-1 | SGG-1 | SGG-1 | SGG-1
H | Melting Alloy TU | B1.30 | B1.88 | B2.40 | B3.30 | B3.70 | B4.85 | B9.10 | B12.8 | B17.5 | B25. | B36. | B45. | CC46.6 | CC64.3 | CC81.5 | CC87.7 | CC112. | CC156. | B3.00 | B3.70 | B4.15
I | NEMA SIZE | 00 | 00 | 00 | 00 | 00 | 0 | 0 | 1 | 1 | 2 | 2 | 2 | 3 | 3 | 3 | 4 | 4 | 4 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 7 | 7 | 7
| Single Phase 115V | [30 empty] | HP | Single Phase |  | 1
| HP | 1/6 | 1/4 | 1/3 | 1/2 | 3/4 | 1 | 1.5 | 2 | 3 | 5 | 7.5 | 10 | [17 empty] | 1 | 1/6 hp | HP |  |  |  | 115V | 230V
| Voltage | 115V | 115V | 115V | 115V | 115V | 115V | 115V | 115V | 115V | 115V | 115V | 115V | [17 empty] | 2 | 1/4 hp | Voltage
A | FLA | 4.4 | 5.8 | 7.2 | 9.8 | 13.8 | 16 | 20 | 24 | 34 | 56 | 80 | - | [17 empty] | 3 | 1/3 hp | FLA |  | A |  | 4.4 | 2.2
B | Wire Size | 14 | 14 | 14 | 14 | 14 | 14 | 12 | 10 | 8 | 4 | 3 | - | [17 empty] | 4 | 1/2 hp | Wire Size |  | B |  | 14 | 14
C | Thermal Breaker Size | 15 | 15 | 15 | 20 | 25 | 30 | 40 | 50 | 70 | 90 | 110 | - | [17 empty] | 5 | 3/4hp | Thermal Breaker Size |  | C |  | 15 | 15
D | Breaker Cat No. | FAL12015 | FAL12015 | FAL12015 | FAL12020 | FAL12025 | FAL12030 | FAL12040 | FAL12050 | FALL2070 | FAL12090 | KAL26110 | - | [17 empty] | 6 | 1 hp | Breaker Cat No. |  | D |  | FAL12015 | FAL22015
E | HD Sw Nema 1 Encl | H221N | H221N | H221N | H221N | H221N | H221N | H221N | H221N | H222N | H223N | H223N | - | [17 empty] | 7 | 1.5hp | HD Sw Nema 1 Encl |  | E |  | H221N | H221N
F | Dual Elem TD Fuse Amps | 6.25 | 9 | 10 | 15 | 20 | 25 | 30 | 30 | 50 | 80 | 100 | - | [17 empty] | 8 | 2 hp | Dual Elem TD Fuse Amps |  | F |  | 6.25 | 3.2
G | Frac HP N1 Class2510 | FG-2 | FG-2 | FG-2 | FG-2 | FG-2 | FG-2 | - | - | - | - | - | - | [17 empty] | 9 | 3 hp | Frac HP N1 Class2510 |  | G |  | FG-2 | FG-2
H | Thermal Unit | A4.32 | A6.20 | A7.65 | A9.85 | A14.8 | A17.9 | - | - | - | - | - | - | [17 empty] | 10 | 5 hp | Thermal Unit |  | H |  | A4.32 | A1.86
I | Integral Hp N1 Enc 2510 | MBG-1 | MBG-1 | MBG-1 | MBG-1 | MBG-1 | MBG-1 | MCG-1 | MCG.1 | MCG-2 | - | - | - | [17 empty] | 11 | 7.5 hp | Integral Hp N1 Enc 2510 |  | I |  | MBG-1 | MBG-1
J | One Melting Alloy | B4.15 | B6.25 | B7.70 | B10.2 | B14.0 | B17.5 | B25.0 | B32.0 | B40.0 | - | - | - | [17 empty] | 12 | 10 hp | One Melting Alloy |  | J |  | B4.15 | B2.10
K | N1 Enclosed 8536 | SAG-11 | SAG.11 | SAG-11 | SBG-1 | SBG-1 | SBG-1 | SCG-1 | SCG-1 | SCG-2 | SEG-6 | SEG-6 | - | [19 empty] | N1 Enclosed 8536 |  | K |  | SAG-11 | SAG.11
L | Thermal Unit | B4.85 | B6.25 | B8.20 | B11.5 | B15.5 | B19.5 | B28.0 | B36.0 | B40.0 | CC64.3 | CC87.7 | - | [19 empty] | Thermal Unit |  | L |  | B4.85 | B2.40
Single Phase 120v
| HP | 1/6 | 1/4 | 1/3 | 1/2 | 3/4 | 1 | 1.5 | 2 | 3 | 5 | 7.5 | 10
| Voltage | 120V | 120V | 120V | 120V | 120V | 120V | 120V | 120V | 120V | 120V | 120V | 120V
A | FLA | 2.2 | 2.9 | 3.6 | 4.9 | 6.9 | 8 | 10 | 12 | 17 | 28 | 40 | 50
B | Wire Size | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 12 | 10 | 8 | 6
C | Thermal Breaker Size | 15 | 15 | 15 | 15 | 15 | 15 | 20 | 25 | 35 | 60 | 80 | 90
D | Breaker Cat No. | FAL22015 | FAL22015 | FAL22015 | FAL22015 | FAL22015 | FAL22015 | FAL22020 | FAL22025 | FAL22035 | FAL22060 | FAL22080 | FAL22090
E | HD Sw Nema 1 Encl | H221N | H221N | H221N | H221N | H221N | H221N | H221N | H221N | H221N | H222N | H222N | H222N
F | Dual Elem TD Fuse Amps | 3.2 | 4.5 | 5.6 | 7 | 10 | 12 | 15 | 20 | 25 | 40 | 60 | 60
G | Frac HP N1 Class2510 | FG-2 | FG-2 | FG-2 | FG-2 | FG-2 | FG-2 | - | - | - | - | - | -
H | Thermal Unit | A1.86 | A2.57 | A2.81 | A5.30 | A6.99 | A8.38 | - | - | - | - | - | -
I | Integral Hp N1 Enc 2510 | MBG-1 | MBG-1 | MBG-1 | MBG.1 | MBG-1 | MBG.1 | MBG-1 | MBG-1 | MCG-1 | MCG-2 | - | -
J | One Melting Alloy | B2.10 | B3.00 | B3.70 | B4.85 | B6.90 | B8.20 | B12.80 | B15.50 | B22.0 | B32.0 | - | -
K | N1 Enclosed 8536 | SAG.11 | SAG-11 | SAG.11 | SAG-11 | SAG-11 | SAG-11 | SBG-1 | SBG-1 | SCG-1 | SCG-2 | SDG-6 | SEG-6
L | Thermal Unit | B2.40 | B3.30 | B4.l5 | B5.50 | B7.70 | B9.10 | B14.0 | B17.5 | B22.0 | B28.0 | B40.0 | CC50.1

## Wire & Conduit
Wire and Conduit Data
BASED ON THE 2005 NEC
Select Wire Size AWG/kcmil
Based on Appendix C - Tables
|  | C1 and C1A |  |  |  |  | Select Wire Size
COPPER |  |  |  | Ampacity at 75C based on NEC Table 310-16 | 460
| THW, THW-2 THHW |  |  | 3 WIRES - INCHES | 3
|  |  |  | 3 Phase 4 Wire - INCHES | 3 1/2
| THHN, THWN, XHHW, |  |  | 3 WIRES - INCHES | 3
| THWN-2, XHHW-2 |  |  | 3 Phase 4 Wire - INCHES | 3 1/2
ALUMINUM |  |  |  | Ampacity at 75C based on NEC Table 310-16 | 375
| THW, THW-2 THHW |  |  | 3 WIRES - INCHES | 3
|  |  |  | 3 Phase 4 Wire - INCHES | 3 1/2
| THHN, THWN, XHHW, |  |  | 3 WIRES - INCHES | 3
| THWN-2, XHHW-2 |  |  | 3 Phase 4 Wire - INCHES | 3
Notes:
Ampacity of conductors based on 30 C ambient.
|  |  |  | Voltage Drop Calculator |  |  | Conduit sizes for aluminum based on the
use of compact conductors
|  |  | Select Wire Size at Top | 700 |  |  | Where a major portion of the load consists of nonlinear loads,
|  |  | Enter Distance in Multiples of 100 ft (i.e. 100ft=1) | 25 |  | Enter Distance | the neutral is considered to be current carrying.
|  |  | Enter Amperage | 15 |  | Enter Amperage | On 4-wire applications, derate the ampacity to 80% per
| Line to Line Volts Drop | 1 Phase Volts | 95% PF | 2.55 |  |  | note 8 and note 10© of the NEC ampacity tables.
| Per Ampere per 100ft. In |  | 80% PF | 3.1875
| Magnetic Conduit Copper Wire | 3 Phase Volts | 95% PF | 2.2125
|  |  | 80% PF | 2.775

## Instructions and Notes
Instructions
Motor Calculator
Three Phase and Single Phase
Click on the Voltage and HP to view information for your application
Transformer Data
Enter the KVA and Voltage to view three-phase and single-phase currents
Scheduler
Enter the Start Date (1/1/05 format) and the number of weeks to view the resulting End Date. Helpful in determining ship dates and project schedules.
Wire and Conduit Page
Use the dropdown list to select wire size to view information.
Voltage Drop
Select wire size as before.
Enter the cable run distance in multiples of 100 ft. (i.e.. 100ft - 1)
Enter the amperage you will be drawing through the wire.
View the voltage drop based on PF.
For other tools: Visit www.Squared.com "Free Software"
Notes: Fuses and circuit breakers shown are for short-circuit ground fault protection only. This data applies to Normal Service applications of switches, starters or breakers shown. Do not use for Heavy Service applications, as defined in the latest Catalog Digest. Data is based on information available at time of publication and is subject to change. See actual installed equipment and Section 110-14C for termination requirements. Fuse sizes and circuit breaker trip amperes are approximate selections suitable for most installations. Thermal unit selectors are not based on NEC currents (see NEC 430-6) but are selected from average full load currents. Thermal units can be more accurately selected using table furnished with starter and full load current marked on the motor name plate.